## Sheet1
11.1 The main features of the TTD pendulum anti-galloping device for 3 subconductors on phase
Nr crt | Characteristics | U.M | Tension | Offered
|  |  | 400 kv | 420 kV max (+5%)
|  |  | Technical requirements | Applied
1 | Conductor type | - | Ol/AIS 300/69 mm² | Ok
|  |  | - 3 conductors per phase | Ok
|  |  | beam distance of 400 mm | 400±3 mm ok
2 | Diameter of the subconductor | mm | 25,15 | ok
3 | Maximum height of the device | mm | 900 | 800
4 | Type of mounting | - | With screw and clip on the armour rods | ok
5 | Armour rod length | mm | >800 | ok
6 | Post delivery waranty | months | 30 | 30
7 | Warranty after commissioning | months | 24 | 24
11.2. Technical characteristics for the TTD pendulum anti-galloping device for 3 sub-conductors on phase
Nr crt | Anti-galloping device for 3 subconductors on phase | U.M | Technical capacities requested | Guaranteed technical capacities
IPRIM-ENERGY LLC
RUSSIA
1 | standards for
| - electrical characteristics | - | SR EN 61854 | IEC 61854:2020
| - mechanical characteristics | - | SR EN 61284 | IEC 61284:1997
| - material | - | SR EN 61897 | IEC 61897:1998
| - mechanical characteristics | -
2 | The maximum line voltage | kV | 420 | 420 (Support Protocol)
3 | Short-circuit current for one second | kA | 31,5 | 31,5 kA (Mech Strength fixed)
4 | RIV level at 1 MHz | dB | 50 | < 50 (Support Protocol)
5 | Technical lifetime | years | at least 30 | >30
6 | Spacer terminals |  | SR EN 61854 | IEC 61854:2020
7 | Constructive realization |  |  | Suspension on Two spacers
8 | Material |  | SR EN 61284 | Damping elements are made of EPDM Fix Bolts/washers/nuts are made of stainless steel
- any material that is suitable for their intended purpose of operation
- cushioning elements should be made of silicone rubber
- clamp bolts and washers are made of stainless steel
9 | The length between the clamping points | mm | 400 | 400±3 mm ok
10 | Fixing/clamping mode |  | Pre-formed spiral clamps | Clamps on Pre-formed spiral armrods
11 | Anti-corrosion protection of metal parts
| - hot zinc galvanizing |  | Yes | ok
| - standard |  | SR EN 61284
| - zinc layer thickness | μm | 86 | ok (Protocol)
12 | Pendulum weight (including coils) | kg | < 55 | 41 or less see Drawings
13 | Recommended tightening torque | Nm | 95 | 95 agreed
14 | Mode of delivery
| - number of devices in the package | pcs | Packages | In agreement with delivery Company
| - number of packages | pcs |  | In agreement with BUYER
15 | Marking mode |  |  | TDD2.4-400-29,25 Number of pcs
| - pendulum |  |  | (if of importance)
- package
16 | Corona effect occurrence voltage | kV | > 1,1x420/1,73 | > 270; Photos for Protocol
17 | Permissible longitudinal slip of the pendulum device
| - metal clamp | mm | 1 | < 1 mm checking at 95 Nm
| - rubber clamp | mm | 2,5
| - pre-formed spiral clamp | mm | 12,0
18 | Cushioning in the frequency range | Hz | 0,1- 1 | 0,15…1,0 In the field
19 | The voltage at which the RIV is measured | kV | > 420/1.73 | ok
20 | Electrical resistance between any non-metallic element of the spacer | MΩ | <20 | ok Protocol
NOTE: The column "Guaranteed technical capacities" must be clearly completed with the value of the technical characteristics of the o equipment or requirements assumed by the economic operator as appropriate. Complete as follows:
- numeric values where numeric values are specified in the column "Technical capacities requested"
- information by text where required in the column "Technical capacities requested"
- in other cases, simply add YES to the requirement
All values filled in the column "Guaranteed technical capacities" shall be supported with the technical specification of the product, issued by the manufacturer, numbered and endorsed by the tenderer by stamp and signature of the legal representative
The tenderer is required to provide proof that the equipment tendered for, to be supplied and installed, complies with the requirements laid down in the specifications
The tenderer may submit, without limitation, any technical documents, leaflets, descriptions, photographs, etc. which he considers necessary for the presentation and technical assessment of the equipment